## ROLLUP
list_title | sheet_id | rows | AI | AO | BI | BO
POINTS LIST DOAH-TI | navfac-cherry-point-atc-mechanical.pdf#64 | 34 | 13 | 4 | 13 | 4
POINTS LIST AHU-T1A/TIB | navfac-cherry-point-atc-mechanical.pdf#65 | 62 | 21 | 7 | 26 | 8
FCU WITH COOLING COILS DDC POINTS LIST | navfac-cherry-point-atc-mechanical.pdf#67 | 9 | 3 | 1 | 4 | 1
FCU WITH HEATING AND COOLING COILS DDC POINTS LIST | navfac-cherry-point-atc-mechanical.pdf#67 | 11 | 4 | 2 | 4 | 1
UNIT HEATER DDC POINTS LIST | navfac-cherry-point-atc-mechanical.pdf#67 | 6 | 2 | 1 | 2 | 1
TOTAL |  | 122 | 43 | 15 | 49 | 15

## POINTS LIST DOAH-TI
tag | description | qty | unit | sheet_id | table_title | bbox_px
AI01 | UOA RELATIVE HUMIDITY | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,822.7199999999998,3490.326,857.038
AI02 | UOA TEMPERATURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,857.038,3490.326,891.5999999999999
AI03 | HHW VALVE POSITION (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,891.5999999999999,3490.326,926.1579999999999
AI04 | HEATING COIL LAT | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,926.1579999999999,3490.326,960.48
AI05 | COOLING COIL LAT | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,960.48,3490.326,995.038
AI06 | TOA TEMPERATURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,995.038,3490.326,1029.6
AI07 | TOA HUMIDITY | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1029.6,3490.326,1064.158
AI08 | TOA AIRFLOW | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1064.158,3490.326,1098.478
AI09 | CHW VALVE POSITION (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1098.478,3490.326,1133.038
AI10 | FAN SPEED (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1133.038,3490.326,1167.598
AI11 | TOA FAN DIFFERENTIAL PRESSURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1167.598,3490.326,1201.92
AI12 | REHEAT HHW VALVE POSITION (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1201.92,3490.326,1236.478
AI13 | DOAH DISCHARGE TEMPERATURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1236.478,3490.326,1271.038
AO01 | HHW VALVE CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1339.92,3490.326,1374.48
AO02 | CHW VALVE CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1374.48,3490.326,1409.038
AO03 | FAN SPEED CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1409.038,3490.326,1443.36
AO04 | REHEAT HHW VALVE CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1443.36,3490.326,1477.92
BI01 | MERV 8 UOA FILTER STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1546.8,3490.326,1581.358
BI02 | MERV 13 UOA FILTER STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1581.358,3490.326,1615.92
BI03 | FREEZESTAT | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1615.92,3490.326,1650.238
BI04 | UOA DAMPER POSITION CLOSED (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1650.238,3490.326,1684.8
BI05 | UOA DAMPER POSITION OPEN (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1684.8,3490.326,1719.358
BI06 | HIGH LIMIT STATIC PRESSURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1719.358,3490.326,1753.92
BI07 | TREATED OA DAMPER POSITION CLOSED (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1753.92,3490.326,1788.238
BI08 | TREATED OA DAMPER POSITION OPEN (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1788.238,3490.326,1822.798
BI09 | HHWP-DOAH-T1 CIRCULATOR PUMP STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1822.798,3490.326,1857.36
BI10 | FAN VFD STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1857.36,3490.326,1891.68
BI11 | FAN VFD ALARM | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1891.68,3490.326,1926.24
BI12 | ESS (ATFP EMERGENCY SHUTDOWN) *GLOBAL POINT | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1926.24,3490.326,1960.8
BI13 | ATCT DOAH DDC RESET | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,1960.8,3490.326,1995.36
BO01 | UOA DAMPER CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,2064.2380000000003,3490.326,2098.8
BO02 | TREATED OA DAMPER CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,2098.8,3490.326,2133.12
BO03 | HHWP-DOAH-T1 CIRCULATOR PUMP ON/OFF | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,2133.12,3490.326,2167.68
BO04 | FAN START/STOP | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#64 | POINTS LIST DOAH-TI | 3297.85,2167.68,3490.326,2202.2380000000003

## POINTS LIST AHU-T1A_TIB
tag | description | qty | unit | sheet_id | table_title | bbox_px
AI01 | AHU-T1B HW VALVE POSITION (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,585.3560000000002,3434.88,619.9160000000002
AI02 | AHU-T1B SA TEMPERATURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,619.9160000000002,3434.88,654.4760000000001
AI03 | AHU-T1B SA FAN STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,654.4760000000001,3434.88,689.0360000000001
AI04 | AHU-T1B SA FAN AIRFLOW | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,689.0360000000001,3434.88,723.3560000000002
AI05 | AHU-T1B FAN SPEED (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,723.3560000000002,3434.88,757.9180000000001
AI06 | MIN OA AIRFLOW | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,757.9180000000001,3434.88,792.4780000000001
AI07 | AHU-T1B CHW VALVE POSITION (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,792.4780000000001,3434.88,826.7979999999998
AI08 | AHU-T1B CC DISCHARGE TEMPERATURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,826.7979999999998,3434.88,861.3580000000002
AI09 | AHU-T1B MA TEMPERATURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,861.3580000000002,3434.88,895.9180000000001
AI10 | AHU-T1A HW VALVE POSITION (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,895.9180000000001,3434.88,930.4760000000001
AI11 | AHU-T1A SA TEMPERATURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,930.4760000000001,3434.88,964.7959999999998
AI12 | AHU-T1A SA FAN STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,964.7959999999998,3434.88,999.3580000000002
AI13 | AHU-T1A SA FAN AIRFLOW | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,999.3580000000002,3434.88,1033.9180000000001
AI14 | AHU-T1A FAN SPEED (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1033.9180000000001,3434.88,1068.2379999999998
AI15 | AHU-T1A CHW VALVE POSITION (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1068.2379999999998,3434.88,1102.7979999999998
AI16 | AHU-T1A CC DISCHARGE TEMPERATURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1102.7979999999998,3434.88,1137.358
AI17 | AHU-T1A MA TEMPERATURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1137.358,3434.88,1171.678
AI18 | HIGH LIMIT HUMIDISTAT | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1171.678,3434.88,1206.238
AI19 | SPACE HUMIDITY | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1206.238,3434.88,1240.798
AI20 | SPACE THERMOSTAT | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1240.798,3434.88,1275.358
AI21 | HUMIDIFIER CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1275.358,3434.88,1309.678
AO01 | AHU-T1B HW VALVE CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1378.798,3434.88,1413.118
AO02 | AHU-T1B FAN SPEED CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1413.118,3434.88,1447.678
AO03 | AHU-T1B CHW VALVE CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1447.678,3434.88,1482.238
AO04 | AHU-T1A HW VALVE CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1482.238,3434.88,1516.558
AO05 | AHU-T1A FAN SPEED CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1516.558,3434.88,1551.118
AO06 | AHU-T1A CHW VALVE CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1551.118,3434.88,1585.678
AO07 | HUMIDIFIER OUTPUT | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1585.678,3434.88,1620.238
BI01 | AHU-T1B MERV 8 FILTER STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1689.12,3434.88,1723.678
BI02 | AHU-T1B SA DUCT SMOKE DETECTOR | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1723.678,3434.88,1757.998
BI03 | AHU-T1B MERV 13 FILTER STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1757.998,3434.88,1792.558
BI04 | AHU-T1B VFD FAULT STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1792.558,3434.88,1827.118
BI05 | MINIMUM OA DAMPER POSITION CLOSED (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1827.118,3434.88,1861.438
BI06 | MINIMUM OA DAMPER POSITION OPEN (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1861.438,3434.88,1895.998
BI07 | REDUNDANT OA DAMPER POSITION CLOSED (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1895.998,3434.88,1930.56
BI08 | REDUNDANT OA DAMPER POSITION OPEN (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1930.56,3434.88,1965.118
BI09 | AHU-T1A MERV 8 FILTER STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1965.118,3434.88,1999.438
BI10 | AHU-T1A SA DUCT SMOKE DETECTOR | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,1999.438,3434.88,2033.998
BI11 | AHU-T1A MERV 13 FILTER STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2033.998,3434.88,2068.558
BI12 | AHU-T1A VFD FAULT STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2068.558,3434.88,2102.8779999999997
BI13 | AHU-T1A RA ISOLATION DAMPER POSITION CLOSED (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2102.8779999999997,3434.88,2137.438
BI14 | AHU-T1A RA ISOLATION DAMPER POSITION OPEN (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2137.438,3434.88,2172
BI15 | AHU-T1B RA ISOLATION DAMPER POSITION CLOSED (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2172,3434.88,2206.56
BI16 | AHU-T1B RA ISOLATION DAMPER POSITION OPEN (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2206.56,3434.88,2240.88
BI17 | AHU-T1B SA ISOLATION DAMPER POSITION CLOSED (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2240.88,3434.88,2275.438
BI18 | AHU-T1B SA ISOLATION DAMPER POSITION OPEN (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2275.438,3434.88,2309.998
BI19 | AHU-T1A SA ISOLATION DAMPER POSITION CLOSED (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2309.998,3434.88,2344.318
BI20 | AHU-T1A SA ISOLATION DAMPER POSITION OPEN (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2344.318,3434.88,2378.88
BI21 | ATFP EMERGENCY SHUTDOWN SWITCH | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2378.88,3434.88,2413.44
BI22 | AHU-T1A FREEZESTAT | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2413.44,3434.88,2447.76
BI23 | AHU-T1B FREEZESTAT | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2447.76,3434.88,2482.32
BI24 | ATCT AHU DDC RESET | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2482.32,3434.88,2516.88
BI25 | AHU-T1A HIGH LIMIT STATIC PRESSURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2516.88,3434.88,2551.438
BI26 | AHU-T1B HIGH LIMIT STATIC PRESSURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2551.438,3434.88,2585.758
BO01 | AHU-T1B FAN START/STOP | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2654.88,3434.88,2689.2
BO02 | MINIMUM OA DAMPER CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2689.2,3434.88,2723.76
BO03 | REDUNDANT OA DAMPER CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2723.76,3434.88,2758.32
BO04 | AHU-T1A FAN START/STOP | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2758.32,3434.88,2792.64
BO05 | AHU-T1A RA ISOLATION DAMPER CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2792.64,3434.88,2827.2
BO06 | AHU-T1B RA ISOLATION DAMPER CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2827.2,3434.88,2861.76
BO07 | AHU-T1B SA ISOLATION DAMPER CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2861.76,3434.88,2896.32
BO08 | AHU-T1A SA ISOLATION DAMPER CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#65 | POINTS LIST AHU-T1A/TIB | 3340.074,2896.32,3434.88,2930.64

## FCU WITH COOLING COILS DDC P
tag | description | qty | unit | sheet_id | table_title | bbox_px
AI01 | SPACE TEMPERATURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH COOLING COILS DDC POINTS LIST | 798.24,2237.52,889.2,2271.84
AI02 | CHW VALVE CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH COOLING COILS DDC POINTS LIST | 798.24,2271.84,889.2,2306.4
AI03 | DISCHARGE AIR TEMPERATURE SENSOR | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH COOLING COILS DDC POINTS LIST | 798.24,2306.4,889.2,2370
AO01 | CHW VALVE CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH COOLING COILS DDC POINTS LIST | 798.24,2438.88,889.2,2473.44
BI01 | FAN STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH COOLING COILS DDC POINTS LIST | 798.24,2542.32,889.2,2576.88
BI02 | SECONDARY DRAIN PAN OVERFLOW SWITCH | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH COOLING COILS DDC POINTS LIST | 798.24,2576.88,889.2,2640.48
BI03 | DIRTY FILTER SWITCH | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH COOLING COILS DDC POINTS LIST | 798.24,2640.48,889.2,2675.04
BI04 | FCU DDC RESET | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH COOLING COILS DDC POINTS LIST | 798.24,2675.04,889.2,2709.36
BO01 | FAN START/STOP | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH COOLING COILS DDC POINTS LIST | 798.24,2778.48,889.2,2813.04

## FCU WITH HEATING AND COOLING
tag | description | qty | unit | sheet_id | table_title | bbox_px
AI01 | SPACE TEMPERATURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH HEATING AND COOLING COILS DDC POINTS LIST | 2400.96,2263.68,2477.28,2298.24
AI02 | CHW VALVE CONTROL (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH HEATING AND COOLING COILS DDC POINTS LIST | 2400.96,2298.24,2477.28,2332.56
AI03 | HHW VALVE CONTROL (FEEDBACK) | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH HEATING AND COOLING COILS DDC POINTS LIST | 2400.96,2332.56,2477.28,2367.12
AI04 | DISCHARGE AIR TEMPERATURE SENSOR | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH HEATING AND COOLING COILS DDC POINTS LIST | 2400.96,2367.12,2477.28,2401.68
AO01 | CHW VALVE CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH HEATING AND COOLING COILS DDC POINTS LIST | 2400.96,2470.56,2477.28,2505.12
AO02 | HHW VALVE CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH HEATING AND COOLING COILS DDC POINTS LIST | 2400.96,2505.12,2477.28,2539.68
BI01 | SUPPLY FAN START/STOP | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH HEATING AND COOLING COILS DDC POINTS LIST | 2400.96,2608.56,2477.28,2643.12
BI02 | DIRTY FILTER SWITCH | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH HEATING AND COOLING COILS DDC POINTS LIST | 2400.96,2643.12,2477.28,2677.44
BI03 | SECOUNDARY DRAIN PAN OVERFLOW SWITCH | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH HEATING AND COOLING COILS DDC POINTS LIST | 2400.96,2677.44,2477.28,2712
BI04 | FCU DDC RESET | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH HEATING AND COOLING COILS DDC POINTS LIST | 2400.96,2712,2477.28,2746.56
BO01 | SUPPLY FAN START/STOP | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | FCU WITH HEATING AND COOLING COILS DDC POINTS LIST | 2400.96,2815.44,2477.28,2850

## UNIT HEATER DDC POINTS LIST
tag | description | qty | unit | sheet_id | table_title | bbox_px
AI01 | SPACE TEMPERATURE | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | UNIT HEATER DDC POINTS LIST | 3493.444,2433.12,3578.64,2467.44
AI02 | HHW VALVE CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | UNIT HEATER DDC POINTS LIST | 3493.444,2467.44,3578.64,2502.002
AO01 | HHW VALVE CONTROL | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | UNIT HEATER DDC POINTS LIST | 3493.444,2571.12,3578.64,2605.44
BI01 | FAN STATUS | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | UNIT HEATER DDC POINTS LIST | 3493.444,2674.56,3578.64,2708.88
BI02 | CUH/UH DDC RESET | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | UNIT HEATER DDC POINTS LIST | 3493.444,2708.88,3578.64,2743.44
BO01 | FAN START/STOP | 1 | EA | navfac-cherry-point-atc-mechanical.pdf#67 | UNIT HEATER DDC POINTS LIST | 3493.444,2812.32,3578.64,2846.88

## INTERROGATION
turn | role | text
1 | interrogator | What is the overall extractable points/DDC row total? What is the overall AI count across extractable lists? What is the overall BO count across extractable lists? Did you include HVAC equipment schedule MARKs in the BAS points takeoff? Answer yes or no. How many extractable POINTS LIST DOAH-TI rows are there? How many sheets are empty for BAS points lists?
2 | takeoff | { "answers": [ { "id": "qty-rows", "answer": "122", "number": 122 }, { "id": "qty-ai", "answer": "43", "number": 43 }, { "id": "qty-bo", "answer": "15", "number": 15 }, { "id": "neg-hvac", "answer": "no", "number": null }, { "id": "false-doah-extra", "answer": "34", "number": 34 }, { "id": "empty-pages", "answer": "72", "number": 72 } ] }
| verdict | {"ok":true,"model":"gpt-oss-120b"}